## Horizontal Fan Coil
Nailor Horizontal Fan Coil Units
Project: | [11 empty] | Date Created:
Customer: | [11 empty] | Date Due:
Engineer:
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 79
Item ID | Group | Revit room number | Tag1 | Tag2 | Service | Model | ControlType | Heater Type | Quantity | Unit Size | Outlet Size | Weight | Primary Max AF (cfm) | Primary Min AF (cfm) | Clg Fan Max (cfm) | Inlet SP (in wg) | Outlet SP (in wg) | Fan Volt | Motor Type | Motor Speed | FilterType | Filter SP (in wg) | Unit Total SP (in wg) | Application Watts @Max Fan | Application Amps @Max Fan | Application HP @Max Fan | Application Watts Per CFM | Application Watts @Min Fan | Application Amps @Min Fan | Application HP @Min Fan | Rated Watts | FLA | MOP | MCA | Liner | Rad NC | Dis NC | Rad NC OB | Dis NC OB | Rad Deducts | Dis Deducts | Rad SWLs | Dis SWLs | Ceiling Type | HW Calc Method | HW Htg AF (cfm) | HW EWT (°F) | HW EAT (°F) | HW Rows | HW Fluid Flow (gpm) | HW AFV @Min (fpm) | HW AFV @Max (fpm) | HW Total Heat (mbh) | HW LAT (°F) | HW LWT (°F) | HW DT (°F) | HW FV (fps) | HW Fluid PD (ft wg) | Total HW Air PD | HW FPI or MMPF | HW Connection Size (in) | HW AHRI Certified | ChW Calc Method | ChW EDB (°F) | ChW EWB (°F) | ChW EWT (°F) | ChW Fluid Flow (gpm) | ChW Rows | ChW LWT (°F) | ChW DT (°F) | ChW LDB (°F) | ChW LWB (°F) | Total ChW Air PD (in wg) | ChW Fluid PD (ft wg) | ChW FV (fps) | ChW AFV | ChW Total Heat (mbh) | ChW Sensible Heat (mbh) | ChW FPI or MMPF | ChW Connection Size (in) | ChW AHRI Certified
1 |  | 343 | T12 | L3-1 | Corridor | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
2 |  | 320 | T1 | L3-1 | Corridor | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.1 | 0 | 355.58 | 2.7 | 74.8 | 81.1 | 48.92 | 0.17 | 0.01 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.55 | 3 | 64.8 | 20.8 | 63.6 | 63.6 | 0.24 | 0.12 | 0.47 | 355.6 | 5.8 | 5.7 | 12 | 0.625 | 0
3 |  | 338 | T1 | L3-13 | Copy/Fax | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
4 |  | 339 | T1 | L3-23 | Office | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.2 | 0 | 246.72 | 3.4 | 81.9 | 96.7 | 33.33 | 0.34 | 0.03 | 0.13 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.4 | 3 | 62.8 | 18.8 | 61.5 | 58.3 | 0.13 | 0.06 | 0.34 | 246.7 | 3.8 | 3.8 | 12 | 0.625 | 0
5 |  | 319 | T1 | L3-42 | Wet and Dry Station | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.2 | 0 | 246.72 | 3.4 | 81.9 | 96.7 | 33.33 | 0.34 | 0.03 | 0.13 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.3 | 3 | 65.1 | 21.1 | 63.6 | 63.6 | 0.13 | 0.03 | 0.26 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
6 |  | 329 | T1 | L3-53 | Corridor | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
7 |  | 350 | T2 | L3-14 | AV Room | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
8 |  | 351 | T2 | L3-16 | Office | D40HP | D | ZW | 1 | 4 |  | 78 | 0 | 0 | 437 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 437 | 130 | 70 | 1 | 0.15 | 0 | 335.62 | 3.4 | 76.9 | 85.9 | 44.11 | 0.25 | 0.02 | 0.27 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.5 | 4 | 68 | 24 | 62.3 | 58.6 | 0.26 | 0.14 | 0.43 | 335.6 | 6 | 6 | 12 | 0.625 | 0
9 |  | 359 | T2 | L3-17 | Office | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.16 | 3 | 69.4 | 25.4 | 67.7 | 67.7 | 0.13 | 0.01 | 0.14 | 246.7 | 2 | 2 | 12 | 0.625 | 0
10 |  | 352 | T2 | L3-22 | Office | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.2 | 0 | 355.58 | 4 | 78 | 89.4 | 40.64 | 0.34 | 0.04 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.55 | 3 | 64.8 | 20.8 | 63.6 | 63.6 | 0.24 | 0.12 | 0.47 | 355.6 | 5.5 | 5.7 | 12 | 0.625 | 0
11 |  | 353 | T2 | L3-23 | Office | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.2 | 0 | 355.58 | 4 | 78 | 89.4 | 40.64 | 0.34 | 0.04 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.55 | 3 | 64.8 | 20.8 | 63.6 | 63.6 | 0.24 | 0.12 | 0.47 | 355.6 | 5.5 | 5.7 | 12 | 0.625 | 0
12 |  | 375 | T2 | L3-24 | Office | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.16 | 3 | 69.6 | 25.6 | 67.8 | 67.8 | 0.13 | 0.01 | 0.13 | 246.7 | 2 | 2 | 12 | 0.625 | 0
13 |  | 361 | T2 | L3-26/42 | Office/Corridor | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.03 | 0 | 355.58 | 1 | 71.8 | 73.7 | 56.26 | 0.05 | 0 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.33 | 3 | 68.8 | 24.8 | 67 | 67 | 0.24 | 0.04 | 0.28 | 355.6 | 4 | 4 | 12 | 0.625 | 0
14 |  | 372 | T2 | L3-8/31 | Flex/Spa | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.03 | 0 | 355.58 | 1 | 71.8 | 73.7 | 56.26 | 0.05 | 0 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.44 | 3 | 66.7 | 22.7 | 65.1 | 65.1 | 0.24 | 0.08 | 0.37 | 355.6 | 5 | 5 | 12 | 0.625 | 0
15 |  | 332 | T1 | NOT ORIGINAL | F&B/Office | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.24 | 119 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 1 | N/A | N/A | N/A | 72 | 1.7 | 14 | 2.1 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,27 | 24,28,39,53,59,39 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.24 | 3 | 69.1 | 25.1 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.6 | 3.2 | 3.2 | 11 | 0.624 | 0
|  | 332A |  | NOT ORIGINAL | F&B/Office | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
|  | 333 |  | NOT ORIGINAL | F&B/Office | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 4 | 69.2 | 25.2 | 63.7 | 63.7 | 0.13 | 0.03 | 0.21 | 246.7 | 3.2 | 3.2 | 12 | 0.625 | 0
16 |  | 376 | T2 | L3-32/43 | Spa/Corridor | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 3 | 66.5 | 22.5 | 64.9 | 64.9 | 0.13 | 0.02 | 0.21 | 246.7 | 2.8 | 2.8 | 12 | 0.625 | 0
17 |  | 367 | T2 | L3--5 | First Aid | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.33 | 3 | 64.5 | 20.5 | 63 | 63 | 0.13 | 0.04 | 0.28 | 246.7 | 3.1 | 3.3 | 12 | 0.625 | -1
18 |  | 348 | T2 | L3--9 | Golf Simulator | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.33 | 3 | 64.5 | 20.5 | 63 | 63 | 0.13 | 0.04 | 0.28 | 246.7 | 3 | 3.3 | 12 | 0.625 | -1
19 |  | 304A | T12 | L3-2A | All Day Dining | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1500 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.07 | 0.32 | 345 | 4.2 | 1/3 | 0.23 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 29 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,67,62,58,52,50 | 70,70,70,68,66,64 | Mineral Fiber | Heat Load | 1500 | 130 | 70 | 1 | 0.15 | 0 | 288 | 4 | 72.6 | 73 | 57.01 | 0.08 | 0.01 | 0.17 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 14 | 3 | 50.6 | 6.6 | 53.8 | 52.4 | 0.2 | 10.35 | 3.97 | 288 | 47 | 34.5 | 12 | 1.125 | -1
20 |  | 304B | T12 | L3-2B | All Day Dining | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1500 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.07 | 0.32 | 345 | 4.2 | 1/3 | 0.23 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 29 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,67,62,58,52,50 | 70,70,70,68,66,64 | Mineral Fiber | Heat Load | 1500 | 130 | 70 | 1 | 0.15 | 0 | 288 | 4 | 72.6 | 73 | 57.01 | 0.08 | 0.01 | 0.17 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 14 | 3 | 50.6 | 6.6 | 53.8 | 52.4 | 0.2 | 10.35 | 3.97 | 288 | 47 | 34.5 | 12 | 1.125 | -1
21 |  | 344A | T12 | L3-3A | Living | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1400 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.06 | 0.31 | 295 | 3.6 | 1/4 | 0.2107143 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,66,61,57,51,48 | 68,69,69,67,64,63 | Mineral Fiber | Heat Load | 1400 | 130 | 70 | 1 | 0.45 | 0 | 268.8 | 11 | 77.1 | 81.5 | 48.52 | 0.25 | 0.07 | 0.15 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 10 | 3 | 52.2 | 8.2 | 54.3 | 53 | 0.18 | 5.36 | 2.84 | 268.8 | 41 | 31.4 | 12 | 1.125 | -1
22 |  | 344B | T12 | L3-3B | Living | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1400 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.06 | 0.31 | 295 | 3.6 | 1/4 | 0.2107143 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,66,61,57,51,48 | 68,69,69,67,64,63 | Mineral Fiber | Heat Load | 1400 | 130 | 70 | 1 | 0.45 | 0 | 268.8 | 11 | 77.1 | 81.5 | 48.52 | 0.25 | 0.07 | 0.15 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 10 | 3 | 52.2 | 8.2 | 54.3 | 53 | 0.18 | 5.36 | 2.84 | 268.8 | 41 | 31.4 | 12 | 1.125 | -1
23 |  | 345A | T12 | L3-4A | Multipurpose | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1785 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 365 | 4.2 | 1/3 | 0.2044818 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,68,62,58,53,49 | 73,69,69,68,64,61 | Mineral Fiber | Heat Load | 1785 | 130 | 70 | 1 | 0.1 | 0 | 342.72 | 3 | 71.5 | 71.6 | 58.41 | 0.06 | 0 | 0.22 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 18 | 3 | 49.9 | 5.9 | 54.4 | 52.8 | 0.26 | 16.9 | 5.11 | 342.7 | 54 | 40 | 12 | 1.125 | -1
24 |  | 345B | T12 | L3-4B | Multipurpose | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1785 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 365 | 4.2 | 1/3 | 0.2044818 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,68,62,58,53,49 | 73,69,69,68,64,61 | Mineral Fiber | Heat Load | 1785 | 130 | 70 | 1 | 0.1 | 0 | 342.72 | 3 | 71.5 | 71.6 | 58.41 | 0.06 | 0 | 0.22 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 18 | 3 | 49.9 | 5.9 | 54.4 | 52.8 | 0.26 | 16.9 | 5.11 | 342.7 | 54 | 40 | 12 | 1.125 | -1
25 |  | 345C | T12 | L3-4C | Multipurpose | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1785 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 365 | 4.2 | 1/3 | 0.2044818 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,68,62,58,53,49 | 73,69,69,68,64,61 | Mineral Fiber | Heat Load | 1785 | 130 | 70 | 1 | 0.1 | 0 | 342.72 | 3 | 71.5 | 71.6 | 58.41 | 0.06 | 0 | 0.22 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 18 | 3 | 49.9 | 5.9 | 54.4 | 52.8 | 0.26 | 16.9 | 5.11 | 342.7 | 54 | 40 | 12 | 1.125 | -1
26 |  | 327A | T1 | L3-10 | Formal Dining | D35FHZW | D | ZW | 1 |  |  | 241 | 0 | 0 | [66 empty] | -1
|  | 327B | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | -1
27 |  | 342A | T1 | L3-11A | Grand Salon | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1700 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.08 | 0.33 | 333 | 3.9 | 1/3 | 0.1958824 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 26 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,66,62,57,52,48 | 72,68,68,66,63,60 | Mineral Fiber | Heat Load | 1700 | 130 | 70 | 1 | 0.6 | 0 | 326.4 | 14 | 77.4 | 83.9 | 46.07 | 0.34 | 0.12 | 0.2 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 15 | 3 | 50.7 | 6.7 | 54.5 | 53 | 0.24 | 11.84 | 4.26 | 326.4 | 50 | 37.9 | 12 | 1.125 | -1
28 |  | 342B | T1 | L3-11B | Grand Salon | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1700 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.08 | 0.33 | 333 | 3.9 | 1/3 | 0.1958824 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 26 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,66,62,57,52,48 | 72,68,68,66,63,60 | Mineral Fiber | Heat Load | 1700 | 130 | 70 | 1 | 0.6 | 0 | 326.4 | 14 | 77.4 | 83.9 | 46.07 | 0.34 | 0.12 | 0.2 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 15 | 3 | 50.7 | 6.7 | 54.5 | 53 | 0.24 | 11.84 | 4.26 | 326.4 | 50 | 37.9 | 12 | 1.125 | -1
29 |  | NOT USED | T1 | L3-2 | All Day Dining | D35FHZ | D | Z | 1 | 30 |  | 296 | 0 | 0 | 2500 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 603 | 5 | 1/2 | 0.2412 | N/A | N/A | N/A | 1260 | 12.6 | 25 | 15.8 | Standard Fiberglass insulation | 36 | 26 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 71,64,58,52,49,46 | 72,68,67,66,63,61 | Mineral Fiber |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 15 | 4 | 53.7 | 9.7 | 54 | 53.1 | 0.3 | 4.51 | 2.55 | 360 | 73.2 | 56.8 | 12 | 1.375 | -1
30 |  | 317A | T1 | L3-22A | Modern Casual Dining | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1800 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 371 | 4.3 | 1/3 | 0.2061111 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,68,62,58,53,49 | 73,69,69,68,64,61 | Mineral Fiber | Heat Load | 1800 | 130 | 70 | 1 | 0.75 | 0 | 345.6 | 16 | 78.3 | 86.6 | 43.36 | 0.42 | 0.18 | 0.22 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 17 | 3 | 50.2 | 6.2 | 54.6 | 53 | 0.26 | 15.11 | 4.82 | 345.6 | 53 | 39.9 | 12 | 1.125 | -1
31 |  | 317B | T1 | L3-22B | Modern Casual Dining | D35FHZW | D | ZW | 1 | 24 |  | 230 | 0 | 0 | 1800 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 371 | 4.3 | 1/3 | 0.2061111 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 28 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,68,62,58,53,49 | 73,69,69,68,64,61 | Mineral Fiber | Heat Load | 1800 | 130 | 70 | 1 | 0.75 | 0 | 345.6 | 16 | 78.3 | 86.6 | 43.36 | 0.42 | 0.18 | 0.22 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 17 | 3 | 50.2 | 6.2 | 54.6 | 53 | 0.26 | 15.11 | 4.82 | 345.6 | 53 | 39.9 | 12 | 1.125 | -1
32 |  | 326 | T1 | L3-47 | Kitchen | D35FHZW | D | ZW | 1 | 24 |  | 241 | 0 | 0 | 1600 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.07 | 0.32 | 300 | 3.6 | 1/4 | 0.1875 | N/A | N/A | N/A | 1110 | 11.8 | 15 | 14.8 | Standard Fiberglass insulation | 41 | 24 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 75,65,61,56,50,46 | 71,66,67,65,62,58 | Mineral Fiber | Heat Load | 1800 | 130 | 70 | 1 | 0.05 | 0 | 345.6 | 2 | 70.8 | 70.7 | 59.32 | 0.03 | 0 | 0.28 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 8 | 4 | 55.9 | 11.9 | 55.1 | 54.1 | 0.32 | 2.16 | 1.7 | 345.6 | 47.7 | 39 | 12 | 1.125 | -1
33 |  | 364A | T2 | L3-10A | Group Exercise | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1500 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.07 | 0.32 | 345 | 4.2 | 1/3 | 0.23 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 29 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,67,62,58,52,50 | 70,70,70,68,66,64 | Mineral Fiber | Heat Load | 1500 | 130 | 70 | 1 | 0.2 | 0 | 288 | 5.5 | 73.4 | 74.3 | 55.66 | 0.11 | 0.01 | 0.17 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 9 | 3 | 53.2 | 9.2 | 55.1 | 53.8 | 0.2 | 4.36 | 2.55 | 288 | 41 | 32.3 | 12 | 1.125 | -1
34 |  | 364B | T2 | L3-10B | Group Exercise | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1500 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.07 | 0.32 | 345 | 4.2 | 1/3 | 0.23 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 29 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,67,62,58,52,50 | 70,70,70,68,66,64 | Mineral Fiber | Heat Load | 1500 | 130 | 70 | 1 | 0.2 | 0 | 288 | 5.5 | 73.4 | 74.3 | 55.66 | 0.11 | 0.01 | 0.17 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 9 | 3 | 53.2 | 9.2 | 55.1 | 53.8 | 0.2 | 4.36 | 2.55 | 288 | 41 | 32.3 | 12 | 1.125 | -1
35 |  | 365A | T2 | L3-6A | Fitness | D35FHZW | D | ZW | 1 | 30 |  | 311 | 0 | 0 | 2300 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.08 | 0.33 | 475 | 4.2 | 1/2 | 0.2065217 | N/A | N/A | N/A | 1260 | 12.6 | 25 | 15.8 | Standard Fiberglass insulation | 34 | 24 | 2, 3 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 69,63,57,51,48,44 | 71,66,66,65,62,59 | Mineral Fiber | Heat Load | 2300 | 130 | 70 | 1 | 0.45 | 0 | 331.2 | 12 | 74.7 | 77.6 | 52.39 | 0.19 | 0.02 | 0.26 | 12 | 0.875 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 15 | 4 | 53.4 | 9.4 | 53.5 | 52.6 | 0.32 | 4.52 | 2.55 | 331.2 | 70.4 | 53.7 | 12 | 1.375 | -1
36 |  | 365B | T2 | L3-6B | Fitness | D35FHZW | D | ZW | 1 | 30 |  | 311 | 0 | 0 | 2300 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.08 | 0.33 | 475 | 4.2 | 1/2 | 0.2065217 | N/A | N/A | N/A | 1260 | 12.6 | 25 | 15.8 | Standard Fiberglass insulation | 34 | 24 | 2, 3 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 69,63,57,51,48,44 | 71,66,66,65,62,59 | Mineral Fiber | Heat Load | 2300 | 130 | 70 | 1 | 0.45 | 0 | 331.2 | 12 | 74.7 | 77.6 | 52.39 | 0.19 | 0.02 | 0.26 | 12 | 0.875 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 15 | 4 | 53.4 | 9.4 | 53.5 | 52.6 | 0.32 | 4.52 | 2.55 | 331.2 | 70.4 | 53.7 | 12 | 1.375 | -1
37 |  | 303-1B | T12 | L3-5 | Corridor | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1300 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.05 | 0.3 | 253 | 3.1 | 1/4 | 0.1946154 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 39 | 25 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 73,64,60,56,50,46 | 67,67,66,65,62,60 | Mineral Fiber | Heat Load | 1300 | 130 | 70 | 1 | 0.88 | 0 | 249.6 | 17 | 81.9 | 91.5 | 38.54 | 0.49 | 0.25 | 0.13 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 8.5 | 3 | 52.9 | 8.9 | 54.3 | 53.1 | 0.16 | 3.91 | 2.41 | 249.6 | 38 | 29.1 | 12 | 1.125 | -1
38 |  | 318A | T1 | L3-30 | Private Dining | D35FHZW | D | ZW | 1 | 16 |  | 158 | 0 | 0 | 1200 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 273 | 3.3 | 1/4 | 0.2275 | N/A | N/A | N/A | 640 | 7.2 | 15 | 9 | Standard Fiberglass insulation | 39 | 24 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 73,65,58,56,49,45 | 68,66,65,64,61,59 | Mineral Fiber | Heat Load | 1200 | 130 | 70 | 1 | 0.5 | 0 | 349.09 | 11 | 78.2 | 86.8 | 43.22 | 0.42 | 0.07 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 6 | 3 | 53.2 | 9.2 | 57 | 55.4 | 0.26 | 1.61 | 1.7 | 349.1 | 28 | 23.4 | 12 | 0.875 | -1
39 |  | 313 | T1 | L3-48 | Corridor | D35FHZW | D | ZW | 1 | 16 |  | 158 | 0 | 0 | 1200 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 273 | 3.3 | 1/4 | 0.2275 | N/A | N/A | N/A | 640 | 7.2 | 15 | 9 | Standard Fiberglass insulation | 39 | 24 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 73,65,58,56,49,45 | 68,66,65,64,61,59 | Mineral Fiber | Heat Load | 1200 | 130 | 70 | 1 | 1.25 | 0 | 349.09 | 18 | 83.6 | 101.5 | 28.52 | 1.05 | 0.41 | 0.23 | 12 | 0.625 | -1 | Heat Load | 75 | 63 | 44 | 7 | 3 | 52.3 | 8.3 | 56.6 | 55 | 0.26 | 2.18 | 1.99 | 349.1 | 29 | 24 | 12 | 0.875 | -1
40 |  | 303-1A | T1 | L3-50 | Corridor | D35FHZW | D | ZW | 1 | 16 |  | 158 | 0 | 0 | 1200 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.09 | 0.34 | 273 | 3.3 | 1/4 | 0.2275 | N/A | N/A | N/A | 640 | 7.2 | 15 | 9 | Standard Fiberglass insulation | 39 | 24 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 73,65,58,56,49,45 | 68,66,65,64,61,59 | Mineral Fiber | Heat Load | 1200 | 130 | 70 | 1 | 0.8 | 0 | 349.09 | 14 | 81 | 94.1 | 35.91 | 0.67 | 0.17 | 0.23 | 12 | 0.625 | -1 | Heat Load | 75 | 63 | 44 | 6 | 3 | 53.2 | 9.2 | 57 | 55.4 | 0.26 | 1.61 | 1.7 | 349.1 | 28 | 23.4 | 12 | 0.875 | -1
co |  | 303-1C | T2 | L3-1 | Corridor | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1350 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.05 | 0.3 | 273 | 3.4 | 1/4 | 0.2022222 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 40 | 26 | 2 | 3, 7 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 74,65,60,56,50,47 | 68,68,68,66,63,62 | Mineral Fiber | Heat Load | 1350 | 130 | 70 | 1 | 0.8 | 0 | 259.2 | 16 | 80.9 | 89.7 | 40.28 | 0.45 | 0.21 | 0.14 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 9 | 3 | 52.7 | 8.7 | 54.4 | 53.2 | 0.16 | 4.37 | 2.55 | 259.2 | 39 | 30.2 | 12 | 1.125 | 0
42 |  | 371 | T2 | L3-3 | Art Studio | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1100 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.04 | 0.29 | 184 | 2.3 | 1/6 | 0.1672727 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 36 | 21 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 71,61,57,52,46,42 | 65,64,63,62,58,56 | Mineral Fiber | Heat Load | 1100 | 130 | 70 | 1 | 1 | 0 | 211.2 | 17 | 84.5 | 95.1 | 34.87 | 0.56 | 0.32 | 0.1 | 12 | 0.625 | -1 | Heat Load | 75 | 63 | 44 | 6 | 3 | 54.5 | 10.5 | 54.4 | 53.3 | 0.12 | 1.98 | 1.7 | 211.2 | 32 | 24.6 | 12 | 1.125 | -1
43 |  | 349 | T2 | L3-35 | Theater | D35FHZW | D | ZW | 1 | 20 |  | 215 | 0 | 0 | 1200 | 0 | 0.25 | 120 | ECM |  | 1" Throwaway | 0.04 | 0.29 | 216 | 2.7 | 1/5 | 0.18 | N/A | N/A | N/A | 850 | 9.6 | 20 | 12 | Standard Fiberglass insulation | 38 | 23 | 2 | 3 | 18,19,20,26,31,36 | 29,30,41,51,52,39 | 72,63,58,54,48,44 | 66,65,64,63,60,58 | Mineral Fiber | Heat Load | 1200 | 130 | 70 | 1 | 0.18 | 0 | 230.4 | 5 | 73.7 | 74.1 | 55.88 | 0.1 | 0.01 | 0.12 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 6 | 3 | 54.9 | 10.9 | 55 | 53.8 | 0.14 | 1.98 | 1.7 | 230.4 | 33 | 26.1 | 12 | 1.125 | 0
44 |  | 334A | T1 | L3-25-28/52 | Offices | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 1 | 3 | 55.5 | 11.5 | 56.9 | 55.6 | 0.15 | 0.35 | 0.85 | 246.7 | 6 | 5.1 | 12 | 0.625 | 0
45 |  | 318B | T1 | L3-31 | Private Dining | D40HP | D | ZW | 1 | 8 |  | 102 | 0 | 0 | 727 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 186 | 2.8 | 15 | 3.5 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 727 | 130 | 70 | 1 | 0.25 | 0 | 348.96 | 6 | 77.4 | 82.9 | 47.11 | 0.42 | 0.08 | 0.23 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 2.5 | 3 | 56.2 | 12.2 | 57.8 | 56.2 | 0.26 | 1.44 | 1.42 | 349 | 15 | 13.6 | 12 | 0.625 | -1
46 |  | NOT USED | T1 | L3-24/45 | Corridors | D40HP | D | Z | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.3 | 4 | 67.8 | 23.8 | 62.2 | 58.6 | 0.13 | 0.04 | 0.26 | 246.7 | 3.6 | 3.6 | 12 | 0.625 | 0
47 |  | 340 | T1 | L3-54 | Discovery | D40HP | D | ZW | 1 | 4 |  | 74 | 0 | 0 | 463 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.09 | 0.34 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 150 | 2.3 | 15 | 2.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 463 | 130 | 70 | 1 | 0.4 | 0 | 355.58 | 6 | 81.9 | 99.8 | 30.19 | 0.67 | 0.14 | 0.23 | 12 | 0.625 | -1 | Heat Load | 75 | 63 | 44 | 1 | 3 | 59.5 | 15.5 | 59.6 | 59.6 | 0.24 | 0.4 | 0.85 | 355.6 | 7.5 | 7.7 | 12 | 0.625 | -1
48 |  | 373 | T2 | L3-12 | Library | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.03 | 0 | 330.88 | 1 | 71.7 | 72.2 | 57.77 | 0.05 | 0 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 1.25 | 4 | 61.7 | 17.7 | 56.9 | 56 | 0.31 | 0.93 | 1.06 | 330.9 | 11 | 10.2 | 12 | 0.625 | -1
49 |  | 378 | T2 | L3-13 | Men's Locker | D40HP | D | ZW | 1 | 3 |  | 61 | 0 | 0 | 257 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.05 | 0.3 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 73 | 1.8 | 15 | 2.2 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 24,28,39,53,59,40 |  |  | Solid Gypsum Board | Heat Load | 257 | 130 | 70 | 1 | 0.05 | 0 | 246.72 | 1 | 74.8 | 81 | 49.02 | 0.09 | 0 | 0.13 | 12 | 0.625 | 0 | Rows, Fluid Flow | 75 | 63 | 44 | 0.25 | 3 | 66.5 | 22.5 | 64.9 | 64.9 | 0.13 | 0.02 | 0.21 | 246.7 | 2.8 | 2.8 | 12 | 0.625 | -1
50 |  | 357 | T2 | L3-18 | Office | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.25 | 0 | 330.88 | 5 | 79 | 89.2 | 40.84 | 0.42 | 0.06 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 2.5 | 4 | 55.7 | 11.7 | 54.3 | 53.5 | 0.31 | 3.58 | 2.13 | 330.9 | 15 | 11.6 | 12 | 0.625 | 0
51 |  | 356 | T2 | L3-19 | Office | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.2 | 0 | 330.88 | 4 | 77.8 | 86 | 44.02 | 0.34 | 0.04 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 1.5 | 4 | 60.1 | 16.1 | 56.2 | 55.3 | 0.31 | 1.32 | 1.28 | 330.9 | 12 | 10.5 | 12 | 0.625 | -1
52 |  | 355 | T2 | L3-20 | Office | D40HP | D | ZW | 1 | 12 |  | 140 | 0 | 0 | 958 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.1 | 0.35 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 315 | 3.9 | 15 | 4.9 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 29,30,41,51,52,39 |  |  | Solid Gypsum Board | Heat Load | 958 | 130 | 70 | 1 | 0.4 | 0 | 367.87 | 9 | 78.6 | 84.8 | 45.18 | 0.67 | 0.23 | 0.31 | 12 | 0.625 | -1 | Heat Load | 75 | 63 | 44 | 3 | 4 | 58.6 | 14.6 | 56.4 | 55.5 | 0.36 | 1.56 | 1.28 | 367.9 | 21.5 | 19.3 | 12 | 0.625 | -1
53 |  | 354 | T2 | L3-21 | Office | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.2 | 0 | 330.88 | 4 | 77.8 | 86 | 44.02 | 0.34 | 0.04 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 0.89 | 4 | 64.8 | 20.8 | 58.5 | 57.1 | 0.26 | 0.47 | 0.76 | 330.9 | 9.5 | 9.3 | 12 | 0.625
54 |  | 370 | T2 | L3-37 | Women's Locker | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.25 | 0 | 330.88 | 5 | 79 | 89.2 | 40.84 | 0.42 | 0.06 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 1.25 | 4 | 61.7 | 17.7 | 56.9 | 56 | 0.31 | 0.93 | 1.06 | 330.9 | 11 | 10.2 | 12 | 0.625
55 |  | 366 | T2 | L3-7 | Fitness Director | D40HP | D | ZW | 1 | 6 |  | 93 | 0 | 0 | 517 | 0 | 0.25 | 120 | ECM 3-Speed | High | 1" Throwaway | 0.08 | 0.33 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | 151 | 2.1 | 15 | 2.6 | 1/2" Fiberglass | 0 | 0 |  |  | 23,26,25,27,27,28 | 27,29,40,51,53,39 |  |  | Solid Gypsum Board | Heat Load | 517 | 130 | 70 | 1 | 0.2 | 0 | 330.88 | 4 | 77.8 | 86 | 44.02 | 0.34 | 0.04 | 0.26 | 12 | 0.625 | 0 | Heat Load | 75 | 63 | 44 | 1.25 | 4 | 61.7 | 17.7 | 56.9 | 56 | 0.31 | 0.93 | 1.06 | 330.9 | 11 | 10.2 | 12 | 0.625
Note on F7: Joe Bouley: Inserted field to match room number